| PO Box 299 Oberon NSW 2787 ABN 98 107 506 208; Version; Author; Reviewed; Reference. A - Rev 1; SM; SEC/PR; F-015. May 2014. HOT WORK PERMIT. |
| --- |
| Permit No. |  |  |  |  | This permit must be completed for all cutting, welding and other hot work performed outside a dedicated workshop area. The permit must be displayed at the work site and returned on completion of work. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Application for hot work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Company/ Person Performing Work for OTHR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Contact Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Tel: |  |  |  |  | ( ) |  |  |  |  |  |  |  |  |  |
| Location of Work: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Description of Work: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Equipment to be used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Permit begins |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Permit expires |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | / / |  |  |  | Time: |  |  |  |  |  | am/pm |  |  |  |  | Date: |  |  |  |  | / / |  | Time: |  |  |  |  | am/pm |  |
| Emergency information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| If a fire occurs, call |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Tel: |  |  |  |  | ( ) |  |  |  |  |  |  |  |  |  |  |
| Nearest fire alarm: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Authorisation Officer to Sign: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The above work is authorised to proceed subject to the following action being taken prior to work starting and procedures being maintained for the duration of the work. Each item is to be checked by the Authorisation Officer prior to work starting for each period (delete and initial if and where Not Applicable). Auth. Officers: President |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Authorised by: |  |  |  |  |  |  |  |  |  |  | Signed: |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  | / / |  |  |
| 1 | Fire Sprinklers and/or Thermal Detectors must be confirmed as operational (where installed). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6 |  | Combustible materials located within 10 m must be removed or protected with non-combustible curtains, metal guards or flameproof covers (not ordinary tarpaulins). In a retail/office environment a minimum of 3m is acceptable. Outdoors - clear grass & other combustibles. |  |  |  |  |  |  |  |  |  |  |  |
| 2 | Indoors: Smoke Detectors must be isolated in the work area and Impairment Procedures followed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 7 |  | All floor & wall openings within 10m must be covered to prevent transmission of sparks. |  |  |  |  |  |  |  |  |  |  |  |
| 3 | Fire equipment - as the situation demands: - Fire Hose Reel - Fire Extinguisher - Mandatory fire watcher present - Fire Tanker, pump & hoses |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 8 |  | The hot work area and any adjoining areas must be patrolled from the start of work until 30 minutes after the work is completed (including break periods). |  |  |  |  |  |  |  |  |  |  |  |
| 4 | Barricades, warning signs & spark/flash screens if required |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 9 |  | Special Conditions. (Please detail) |  |  |  |  |  |  |  |  |  |  |  |
| 5 | Work area, trenches, pits, etc. must be clear of flammable liquids, gases, or vapours. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Work Completed and Area Safe |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The work area has been inspected by the Authorised Representative 30 minutes after completion of work: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Signed: |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  | / / |  |  |  |  | Time: |  |  |  |  |  | am/pm |  |